## Instructions
Somerville Low Load Buildings Energy Input Form v1.1
Updated 5/24/2021
Context:
Somerville Climate Forward, Somerville's Community Climate Action Plan, identifies the need for new development to meet net zero emissions standards to support the citywide goal of achieving net zero greenhouse gas emissions by 2050.
New buildings and extensive renovations should ideally be designed to achieve operational carbon neutrality and to minimize embodied carbon in construction materials.
Reducing heating loads is the single-most important step towards designing a cost-effective, zero-carbon building in Somerville.
This calculator provides an easy way to assess and reduce your building's loads.
The purpose of the Low Load Building Energy Input Form is to:
- Quantify the heating loads of the Proposed building and compare them to: 1) a low load scenario and 2) the MA minimum code requirements.
- Support consistency and transparency in the development and review of a project's approach to cost effective zero-carbon design.
Encourage practical and cost-effective design decisions that enable the efficient electrification of commercial buildings
The Calculator compares four building scenarios:
- Proposed Building: The building as-designed.
- ASHRAE 90.1-2013: A code compliant equivalent to the as-designed building
- Low Load Building: The building with low heating load components, targeting cost-effective Zero Net Carbon (ZNC).
How to use this workbook:
- The table below outlines the primary steps.
All inputs required by the user are highlighted in blue cells.
Step | Tab | Inputs | Outputs | Opportunities
1 | PRE-SUBMITTAL INFO | Enter Proposed Building Parameters | Review Envelope Outputs and Heating load of the Proposed building and compare to Low Load building and MA Code Minimum building. | If the Proposed Heating Load is equal to or less than the Low Load Target AND the proposed design is all electric, then you are done. There is no need to submit energy model results for development review. FOR LABS AND HEALTHCARE ONLY: If the Proposed Heating Load is equal to or less than the Low Load Target AND the Proposed Electric Heat Pump Heating Capacity is equal to or greater than the 35°F Ambient Suggested Minimum Heat Pump Heating Capacity, then you are done. There is no need to submit energy model results for development review.
2 | DEVELOPMENT REVIEW INFO | Enter Energy Model Results | Review the outputs in the Development Review Dashboard to determine LEED Point Earnings. Confirm that your EAc1 point totals are consistent with your LEED checklist.

## PRE-SUBMITTAL INFO
PRE-SUBMITTAL LOAD ASSESSMENT
Reducing heating loads is the single-most important step towards designing a cost-effective zero-carbon building in Somerville.
This calculator provides an easy way to assess and reduce your building's loads.
Instructions:
1 | Fill in the blue cells with your project information: | All user inputs in blue are required.
2 | Review Pre-Submittal Dashboard tab.
3 | Compare the Proposed heating load to the heating load of a MA Code Minimum design, and to a Low Load design.
4 | For more details, review the 'Detailed Loads' tab. It provides a summary of the assumptions in the MA Code and Low Load options.
5 | Consider strategies to cost-effectively reduce the heating load and heating capacity of the Proposed design.
Project Name
Project Address
Submission date
Filing
Individual responsible of submission
Firm responsible for submission
Project team
Owner
Architect
MEP Consultant
| Energy Performance Consultant |  |  |  | if applicable
| Envelope Consultant |  |  |  | if applicable
| Summary of submission |  |  |  | Outline key project goals, progress to date and major takeaways from this submission.
| General Project Inputs |  |  | User Comments |  | Instructions
| Number of Stories Above Grade |  |  |  |  | Do not include mechanical penthouse or unconditioned rooftop amenity spaces as a story.
| Total Building Gross Floor Area | 0 | GSF |  |  | Automatically calculated, based on sum of individual building types input below. Confirm that the value correctly aligns with the total building value.
| Total Building Net Occupiable Floor Area |  | NSF |  |  | Automatically calculated, based on sum of individual building types input below.
| Total Daylight Zone Area (per IECC 2018) | 0 | NSF |  |  | Input Daylight Zone area, per IECC 2018 C405.2.3.2. For simple calculation, measure 1x the window head height from the floor (H). Trace an area on the floor of depth (H) along the length of relevant windows. This floor plan projection represents the IECC 2018 daylight area. Please see IECC 2018 for more detail.
| Total Building Vertical Façade Area | 0 | SF |  |  | Automatically calculated, based on sum of individual building types input below.
| Roof Area |  | SF |  |  | Include total roof area as seen from above. Includes mechanical penthouse roofs and spaces throughout the building where ambient air is located outside of the ceiling plane (even if not on top of building).
| Primary Building Type |  |  | User Comments |  | Instructions
| Primary Building Type |  |  |  |  | Select from menu. Primary building type is the use type representing the greatest % of total building floor area. If the specific type of the Proposed building is not listed in the menu, select the type that is most similar. NOTE: if a single development includes multiple separate buildings, project teams are encouraged to use a separate CNBA calculator for each building. Otherwise, the daylight area and code-reference window area calculations will be incorrect. In such cases: the user must provide a separate a summary spreadsheet with total results summary tables and charts similarly formatted to this spreadsheet, including load, construction cost, and emissions summary, combining of all buildings in the development.
| Gross Square Feet |  | GSF |  |  | Input gross square feet associated with the Primary Building Type. Do not include outdoor unconditioned areas or unconditioned garage spaces. If there are more than 3 building use types, input the total value that does not fall under Secondary and Tertiary categories below.
| Vertical Façade Area |  | SF |  |  | Input total exterior facade area associated with the Primary Building Type, including exterior wall and window area, as defined by IECC 2018. Include only facade areas that separate interior conditioned/heated space from the exterior. Exclude other areas, such as: screen walls, parapets, mechanical louvers, and areas that separate non-conditioned space from the exterior. If there are more than 3 building use types, input the total value that does not fall under Secondary and Tertiary categories below.
| Window Area (SF) |  | SF |  |  | Input window area associated with primary building. Calculated by measuring the rough opening of the window assembly. Spandrel area that does not allow light into the interior of the building is excluded. If there are more than 3 building use types, input the total value that does not fall under Secondary and Tertiary categories below.
| Secondary Building Type |  |  | User Comments |  | Instructions
| Secondary Building Type |  |  |  |  | Secondary building type is the use type representing the second greatest % of total building floor area.
| Gross Square Feet |  | GSF |  |  | Provide inputs for the Secondary Building Type, similar to the process used for the Primary Building Type, defined above.
| Vertical Façade Area |  | SF |  |  | Provide inputs for the Secondary Building Type, similar to the process used for the Primary Building Type, defined above.
| Window Area (SF) |  | SF |  |  | Provide inputs for the Secondary Building Type, similar to the process used for the Primary Building Type, defined above.
| Tertiary Building Type |  |  | User Comments |  | Instructions
| Tertiary Building Type |  |  |  |  | Tertiary building type is the use type representing the third greatest % of total building floor area.
| Gross Square Feet |  | GSF |  |  | Provide inputs for the Tertiary Building Type, similar to the process used for the Primary Building Type, defined above.
| Vertical Façade Area |  | SF |  |  | Provide inputs for the Tertiary Building Type, similar to the process used for the Primary Building Type, defined above.
| Window Area (SF) |  | SF |  |  | Provide inputs for the Tertiary Building Type, similar to the process used for the Primary Building Type, defined above.
| Envelope Parameters |  |  | User Comments |  | Instructions
| Window Assembly U-value |  | Btu/h·°F·sf |  |  | U-value times Area (UxA) weighted average for all windows. [(U-value window type 1) x (Area window type 1) + (U-value window type 2) x (Area window type 2) ….] / [Total window area]
| Wall Assembly U-value |  | Btu/h·°F·sf |  |  | UxA weighted average for all walls. [(U-value wall type 1) x (Area wall type 1) + (U-value wall type 2) x (Area wall type 2) ….] / [Total wall area]. For assembly U-values see ASHRAE 90.1-2016 Normative Appendix A
| Roof Assembly U-value |  | Btu/h·°F·sf |  |  | UxA weighted average for all roofs. [(U-value roof type 1) x (Area roof type 1) + (U-value roof type 2) x (Area roof type 2) ….] / [Total roof area] For assembly U-values see ASHRAE 90.1-2016 Normative Appendix A
| Infiltration - Maximum at Blower Door Test |  | cfm/sf at 75pa |  |  | IECC 2018 requires 0.25 cfm/sf @ 75 Pa
| HVAC Parameters |  |  | User Comments |  | Instructions
| Minimum Outdoor Airflow + Make-Up Rate |  | CFM |  |  | Input the minimum outdoor airflow rate required by ASHRAE 62.1 and/or ASHRAE 170 (licensed healthcare facilities), or minimum make-up airflow required. Make-up airflow is applicable to spaces with required minimum air-change rates (such as laboratories) or make-up is required due to a dedicated exhaust system (such as fume hoods, kitchen exhaust, etc.).
| Proposed Outdoor Airflow + Make-Up Rate |  | CFM |  |  | Input the as-designed outdoor airflow quantity.
| IF LAB OR HEATHCARE Class 3 and 4 Exhaust (CFM) |  | CFM |  |  | Class 3 and 4 Exhaust is defined as exhaust meeting the definition of Class 3 and 4 air in ASHRAE/ASHE Standard 62.1-2019, including laboratory fume hood exhaust, laboratory general exhaust when combined with laboratory fume hood exhaust, exhaust where energy recovery is not allowed by ASHRAE/ASHE Standard 170 for use in energy recovery systems with leakage potential, and systems exhausting toxic, flammable, paint or corrosive fumes or dust. The Class 3 and 4 Exhaust system must be capable of reducing exhaust and makeup airflow rates to 50% of the zone design values or the minimum required to maintain pressurization relationship requirements. Excludes Exempt Exhaust. Excludes Class 2 Exhaust. Excludes Class 1 Exhaust: for example, excludes office exhaust, even when the Proposed design has a combined office and laboratory exhaust system.
| IF EXEMPT SPECIALTY EXHAUST OR COMMERCIAL KITCHENS INCLUDED Exempt Exhaust (CFM) |  | CFM |  |  | Exempt Exhaust is defined as exhaust where energy recovery systems are prohibited by 780 CMR or the International Mechanical Code. This includes exhaust from commercial kitchen hoods used for collecting and removing grease vapors and smoke. It also includes radioactive isotope exhaust. If exhaust heat recovery is included in the proposed design, the exhaust should not be classified as Exempt.
| IF MECHANICALLY HUMIDIFIED Humidification Load |  | MBH |  |  | If the building, or a portion of the building is humidified, input the humidification load here. This value is carried consistently across all options.
| IF APPLICABLE Process Heating Load |  | MBH |  |  | If the building heating plant supplies heating energy for process loads, input the total of all process loads supplied by the building heating system, such as: pool heating, sterilization, domestic hot water. Do NOT include process loads supplied by systems other than the building heating plant. This value is carried consistently across all options.
| Ventilation Heating Sensible Recovery Effectiveness |  | % |  |  | Sensible Energy Recovery Effectiveness is defined as the change in the dry-bulb temperature of the outdoor air supply achieved by the heat recovery device, divided by the difference between the outdoor air and entering exhaust air dry-bulb temperatures, at 0˚F winter design condition, expressed as a percentage. For buildings with multiple types of exhaust heat recovery, this value shall be the cfm-weighted average value.
| Ventilation Cooling Total Enthalpy Recovery Effectiveness |  | % |  |  | Enthalpy Energy Recovery Effectiveness is defined as the change in the enthalpy of the outdoor air supply achieved by the heat recovery device, divided by the difference between the outdoor air and entering exhaust air enthalpy, at summer design condition, expressed as a percentage. For buildings with multiple types of exhaust heat recovery, this value shall be the cfm-weighted average value.
| Class 3 and 4 Exhaust Sensible Recovery Effectiveness |  | % |  |  | Sensible Energy Recovery Effectiveness is defined above. For buildings with multiple types of exhaust heat recovery, this value shall be the cfm-weighted average value.
| Electric Space Heating Plant Capacity (at 35°F ambient) |  | MBH |  |  | Input the proposed capacity (useful heating output at 35°F ambient condition) of the building's electric space heating system (heat pump for labs and healthcare; heat pump or electric resistance for all other building types). EXCLUDE the capacity of redundant equipment that is intended to operate only when heating equipment fails (commonly referred to as an N+1 configuration). Also EXCLUDE the capacity of redundant equipment that is intended to operate when ventilation heat recovery devices fail. This can be generated from preliminary calculations used to size the heating plant in the conceptual stages of design. EXCLUDE humidification and process heating loads (these are accounted for separately below).
| Non-Electric Space Heating Plant Capacity |  | MBH |  |  | Input the proposed capacity (useful heating output at design conditions) of the building's non-electric space heating system (e.g. fossil-fuel or district steam). EXCLUDE the capacity of redundant equipment that is intended to operate only when heating equipment fails (commonly referred to as an N+1 configuration). Also EXCLUDE the capacity of redundant equipment that is intended to operate when ventilation heat recovery devices fail. This can be generated from preliminary calculations used to size the heating plant in the conceptual stages of design. EXCLUDE humidification and process heating loads (these are accounted for separately below).
| Total (Non-Redundant) Space Heating Plant Capacity |  | MBH |  |  | If the electric + non-electric heating system does not include redundancy, add rows 79 and 80. EXCLUDE the capacity of redundant equipment that is intended to operate only when other equipment fails (commonly referred to as an N+1 configuration). If there is redundancy between electric + non-electric heating systems, EXCLUDE redundant capacity. For example, if the non-electric heating plant is designed to handle the entire heating load, and the electric heating plant is redundant, then only enter the non-electric heating plant capacity. This can be generated from preliminary calculations used to size the heating plant in the conceptual stages of design.
| NON-Space-Heating Plant Capacity |  | MBH |  |  | Input the proposed capacity (useful heating output at design conditions) of the building's NON-space-heating system (electric and non-electric included). This value will be carried consistently across all options. This may include capacity for uses such as: humidification, snow melt, pool heating, sterilization, etc.
| Will the building's heating system be 100% electric? |  |  |  |  | This does not align with the City of Somerville's goals for carbon neutral ready buildings
| Will the building's DHW be 100% electric? |  |  |  |  | This does not align with the City of Somerville's goals for carbon neutral ready buildings
| Cooling Plant Capacity |  | Tons |  |  | Input the proposed cooling system capacity. This may include capacity for all uses such as: space cooling, dehumidification, process cooling loads, etc.
| Envelope Outputs |  |  | User Comments |  | Instructions
| Window-to-wall ratio | #DIV/0! |  |  |  | Automatically calculated value. Review and confirm this aligns with the design intent. If inputs above are correct, this is the value following IECC 2018 protocol. Note: this is a simplified calculation and does not account for some envelope components, such as foundations and exposed floor areas.
| Average Envelope U-value (UxA / A) - Design | #DIV/0! | Btu/h·°F·sf |  |  | Automatically calculated value. Review and confirm this aligns with the design intent. If inputs above are correct, this is the value following IECC 2018 protocol. Note: this is a simplified calculation and does not account for some envelope components, such as foundations and exposed floor areas.
| Average Envelope U-value (UxA / A) - Maximum per Code | #DIV/0! | Btu/h·°F·sf |  |  | Automatically calculated value. If inputs above are correct, this is the approximate maximum allowable value following IECC 2018 protocol. Note: this is a simplified calculation and does not account for some envelope components, such as foundations and exposed floor areas.
| Average Envelope U-value (UxA / A) - Aligns with Code? | #DIV/0! | Btu/h·°F·sf |  |  | If "NO" is shown in red, the envelope likely does not comply with MA Energy Code (780 CMR revised 9th edition / IECC 2018, mandatory as of January 2021) and should be revised. Note: this is a simplified calculation and does not account for some envelope components, such as foundations and exposed floor areas. Therefore, it is not proof or equivalence of the envelope backstop code compliance.
| Heating Capacity |  |  | User Comments |  | Instructions
| Low Load Building - Heating Plant Capacity | #NUM! | Btu/h·sf |  |  | Automatically calculated value. Indicates a Low-Load target value, intended to optimize cost-effective electrification and procurement of renewable energy to achieve Zero Net Carbon (ZNC).
| Proposed Building - Heating Plant Capacity | #NUM! | Btu/h·sf |  |  | Automatically calculated value. Indicates the Proposed Design value, per the inputs above. Design teams should pursue low-load, cost-effective solutions to meet the City of Somerville's Climate Action goals.
| MA Code Minimum Building - Heating Plant Capacity | #NUM! | Btu/h·sf |  |  | Automatically calculated value. Indicates the value for a building that meets the MA Code Minimum envelope and exhaust heat recovery performance.
Heating Loads
| Low Load Building | #DIV/0! | Btu/h·sf
| Proposed Building | #DIV/0! | Btu/h·sf
| MA Code Minimum Building | #DIV/0! | Btu/h·sf
[JWK] LET'S DELETE THIS CHART

## Construction Cost (hidden)
CONSTRUCTION COST ASSESSMENT
Through integrated design, Zero Carbon buildings can achieve cost parity with conventional buildings.
This calculator provides an easy way to assess and reduce the cost of your approach to carbon neutral.
Instructions:
1 | Fill in the blue cells with the required information: |  |  | All user inputs in blue are required.
2 | Review the Construction Cost Outputs Table (at the top) and the Construction Cost Chart (to the right).
3 | Compare the construction cost of the Proposed design to that of the MA Code Minimum design, and the 'ZNC' design.
4 | Consider strategies to reduce construction cost, while also reducing carbon emissions of the Proposed design.
| Construction Cost Outputs |  |  |  | $/SF | % of Total Construction Cost
| Proposed Building Construction Cost Increase (+) or Savings (-) compared to ZNC Building |  |  |  | #NUM! | #NUM!
| Proposed Building Construction Cost Increase (+) or Savings (-) compared to Proposed 100% Electric |  |  |  | #NUM! | #NUM!
| Total Construction Cost for Project |  |  |  | 700 | 100%
General note: teams may include pro-rated cost of contingency, escalation, CM fees, and items related to individual systems such as controls within individual line items, as appropriate.
|  | Performance / Quantity |  | System descriptions used for pricing | Construction Cost | Cost units | Quantity | Total Cost
Low Load ZNC | ARCHITECTURAL | [9 empty] | Instructions | User Comments | BPDA Comments
| Window (Glazing + Frame) | 0.26 | U-value | (provide system / assembly description used for pricing) | 155 | $/sf window area | 0 | 0 | 0 | 0 | If pricing multiple window assembly types, input an area-weighted average cost per square foot.
| Wall | 0.064 | U-value | (provide system / assembly description used for pricing) | 115 | $/sf wall area | 0 | 0 | 0 | 0 | For buildings with multiple wall assembly types, input an area-weighted average cost per square foot.
| Roof | 0.032 | U-value | (provide system / assembly description used for pricing) | 30 | $/sf roof area | 0 | 0 | 0 | 0 | For buildings with multiple roof assembly types, input an area-weighted average cost per square foot.
| Air Barrier Construction + Testing | 0.1 | cfm/sf@75pa | (provide system / assembly description used for pricing) | 1 | $/sf façade area | 0 | 0 | 0 | 0 | Input the construction cost to achieve the air-tightness metric listed, including air barrier construction management and testing.
| Net Space Impact | 1000 | area saved (SF) | (describe the space requirements compared to the proposed case) | 200 | $/sf floor area | -1000 | -200000 | n/a | 40000 | Approximate NET square footage savings (input positive value) [or increase (input negative value)] to accommodate smaller [or larger] mechanical and electrical systems within the building envelope. Do not include exterior areas, such as pad-mounted or roof-mounted equipment space requirements.
| HVAC | [7 empty] | 0 | 0 | Instructions | User Comments | BPDA Comments
| DOAS AHU | 80% | Heat Recovery | (provide description) | 22 | $/cfm DOAS AHU capacity input manual override capacity here if required per instructions: | 0 | 0 | 0 | 0 | Enthalpy wheels, dual-wheel and regenerative core are examples of technology that can achieve this level of performance. For program areas that are required to rely on "all-air" systems by applicable building standards (such as ASHRAE 170), the DOAS AHU cfm shall be reduced such that the whole building average mixed air temperature (mixed return air and outdoor air after the energy recovery device, but with no heat from the heating coil) at the winter design condition is 62F. This avoids unnecessary over-recovery. The resulting reduced DOAS AHU cfm value shall be input as the manual override capacity in this row. The total volume of outdoor air remains unchanged; a portion is supplied by DOAS AHUs with energy recovery and the remaining volume of outdoor air does not receive energy recovery before mixing with the return air. Program areas not required to rely on "all-air" systems shall remain served by DOAS. If an override value is input in this row, inputs will also be required in the Non-DOAS AHU row below. This calculator automatically accounts for the impact of reduced DOAS AHU air volume (and associated increase in untreated outdoor air) in the load calculations.
| Non-DOAS AHU |  | cfm | Do NOT input value for Non-DOAS AHU, unless an all-air system is required by a code or standard (such as ASHRAE 170) (provide system description) | 14 | $/cfm non-DOAS AHU capacity | 0 | 0 | 700000 | 700000 | The ZNC option relies on DOAS, therefore this category is typically not applicable. But, for spaces required to use all-air systems by applicable building standards, such as ASHRAE 170, users may input values in this row as appropriate. If values are entered in this row, also see instructions in DOAS AHU row above.
| Perimeter Heat | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 320000 | 320000 | The ZNC option relies on a high performance envelope, therefore perimeter heat is n/a.
| Zone Systems | supplemental at zone |  | (provide supplemental heating + cooling system description) | 5 | $/sf floor area | 0 | 0 | 0 | 0 | ZNC option relies on DOAS, therefore supplemental zone heating and cooling is assumed. Design teams should determine a zone heating and cooling system that is optimally cost effective and appropriate for the building use and other relevant design considerations. if the Proposed design relies on supplemental zone heating and cooling systems, the same type of system should typically be used for the ZNC option, with adjustments to account for the difference in loads The NET cost should account for the cost of the zone heating and cooling system, and the savings due to reduction or elimination of the conventional zone conditioning system.
| Electric Space Heating Plant | 1.7 | Air to Water | (provide system description) | 200 | $/MBH (include all plant costs) | 0 | 0 | 0 | #NUM! | Select the heat pump type from the drop-down menu, then provide a description and cost (per unit of capacity listed). The heat pump COP value automatically provided is not the average operating efficiency. The COP is the conversion factor to estimate the heat pump electrical circuit capacity required and is used only to calculate the Plant Peak Electrical Capacity.
| Non-Electric Space Heating Plant | n/a | n/a | (provide system description) | 20 | $/MBH (include all plant costs) | #NUM! | #NUM! | 0 | n/a | If the ZNC option automatically indicates non-electric heating plant capacity is warranted, provide a description and cost of the likely non-electric heating system compatible with the electric heating plant selected.
| NON-Space-Heating Plant |  |  | (provide system description) | 30 | $/MBH (include all plant costs) input manual override capacity here: | 0 | 0 | 0 | 0 | The default capacity of the ZNC option matches the Proposed case for NON-space-heating heating plant capacity. But, if humidification is included, the associated capacity reduction due to enhanced heat recovery should be taken into account. In this case, a reduced value shall be manually entered into the blue cell. Users may determine whether it is appropriate for this heating plant to be electric or non-electric, based on professional judgement.
| Cooling System | 0 | Tons | (provide description. Note: formula automatically takes credit for ventilation load reduction) | 1000 | $/Ton (include all plant costs) | 0 | 0 | 0 | 1000000 | The ZNC option automatically calculates the cooling plant capacity, based on the Proposed design, accounting for the net impact on the cooling load, due to the change in ventilation heat recovery effectiveness. It also takes credit for the cooling capacity of the electric heat pump system (based on the fact that heat pumps typically have at least as much cooling capacity as heating capacity at design conditions). It does not take credit for changes in the envelope. The cooling plant type should be determined based on engineering best practice, accounting for the Proposed cooling plant, the cooling plant capacity automatically calculated for the ZNC option, the electric heating plant type and associated cooling capacity, and optimal cost-effective integrated solutions.
| PLUMBING | [9 empty] | Instructions | User Comments | BPDA Comments
| Domestic/Service Hot Water |  |  | (provide system description) | 100 | $/MBH (include all system costs) Do not exceed 300% of Proposed option cost (see instructions) | 5000 | 500000 | 250000 | 500000 | The capacity of the ZNC option automatically matches the Proposed design. Users should input an appropriate electric domestic/service hot water system description and cost. If the domestic/service hot water system has high demand (such as would be the case for residential, hotel, healthcare, etc.), a hybrid electric/non-electric solution shall be utilized if necessary to avoid exceeding 300% of the domestic/service hot water system cost of the Proposed design. Include electrical infrastructure costs impacts in this assessment.
| ELECTRICAL | [9 empty] | Instructions | User Comments | BPDA Comments
| Plant Peak Electrical Capacity | #DIV/0! | kW | (provide system description) | 1500 | $/kW (include all system costs) | #DIV/0! | #DIV/0! | 1500000 | 2250000 | The ZNC option automatically calculates the value, based on the Proposed design, accounting for the net impact on electrical infrastructure due to the change in heating and cooling plant. It automatically takes into account whether the peak electrical demand is driven by cooling or heating.
| INCENTIVES | [9 empty] | Instructions | User Comments | BPDA Comments
| Total Year 1 Incentive Value |  |  | (provide incentive description) | -2.25 | $/sf | 0 | 0 | 0 | 0 | Input the total anticipated year-1 incentive value (utility, grants, other). Provide value in terms of $/sf.
#NUM!
|  | Performance / Quantity |  | System descriptions used for pricing | Construction Cost | Cost units | Quantity | Total Cost
Proposed | ARCHITECTURAL | [9 empty] | Instructions | User Comments | BPDA Comments
| Window (Glazing + Frame) | 0 | U-value | (provide system / assembly description used for pricing) | 150 | $/sf window area | 0 | 0 |  |  | Provide a description and cost per square foot, accounting for the full system assembly (window and frame). For buildings with multiple window assembly types, input an area-weighted average cost per square foot.
| Wall | 0 | U-value | (provide system / assembly description used for pricing) | 115 | $/sf wall area | 0 | 0 |  |  | Provide a description and cost per square foot, accounting for the full system assembly. For buildings with multiple wall assembly types, input an area-weighted average cost per square foot.
| Roof | 0 | U-value | (provide system / assembly description used for pricing) | 30 | $/sf roof area | 0 | 0 |  |  | Provide a description and cost per square foot, accounting for the full system assembly. For buildings with multiple roof assembly types, input an area-weighted average cost per square foot.
| Air Barrier Construction + Testing | 0 | cfm/sf@75pa | (provide system / assembly description used for pricing) | 0.5 | $/sf façade area | 0 | 0 |  |  | Input the construction cost to achieve the air-tightness metric listed, including air barrier construction management and testing.
| Net Space Impact | (base case for comparison) | [5 empty] | n/a |  |  | Proposed design is the base case, to which the other options are compared. No input required.
| HVAC | [9 empty] | Instructions | User Comments | BPDA Comments
| DOAS AHU | 0% | Heat Recovery | (provide system description) | 20 | $/cfm DOAS AHU capacity | 0 | 0 |  |  | Provide a description of the Proposed design and associated cost. Includes supply and exhaust duct riser and central distribution costs.
| Non-DOAS AHU | 50000 | cfm | (provide system description) | 14 | $/cfm non-DOAS AHU capacity | 50000 | 700000 |  |  | Provide a description of the Proposed design and associated cost. Includes supply, return and associated relief/exhaust duct risers and central distribution costs.
| Perimeter Heat | 8000 | lf | (provide system description) | 40 | $/lf perimeter heat (include riser + pump costs) | 8000 | 320000 |  |  | Provide a description of the Proposed design and associated cost. Includes riser and pump costs.
| Zone Systems |  |  | (provide system description) | 5 | $/sf floor area | 0 | 0 |  |  | Provide a description of the Proposed design and associated cost. Zone system includes cost of terminal heating and cooling systems, such as VAV boxes, fan coil units, radiant systems, chilled beams, etc. Includes low-pressure ductwork and diffusers.
| Electric Space Heating Plant |  | COP at 0˚F | (provide system description) | 200 | $/MBH (include all plant costs) | 0 | 0 |  |  | Provide a description of the Proposed design and associated cost. If ground-source is proposed, include directly associated costs, including the bore field.
| Non-Electric Space Heating Plant |  |  | (provide system description) | 20 | $/MBH (include all plant costs) | 0 | 0 |  |  | Provide a description of the Proposed design and associated cost.
| NON-Space-Heating Plant |  |  | (provide system description) | 30 | $/MBH (include all plant costs) | 0 | 0 |  |  | Provide a description of the Proposed design and associated cost. Include both electric and non-electric combined if both types exist in the design. This value will be carried consistently across all options. This may included capacity for such uses as humidification, pool heating, sterilization, etc.
| Cooling System | 0 | Tons | (provide system description) | 1000 | $/Ton (include all plant costs) | 0 | 0 |  |  | Provide a description of the Proposed design and associated cost.
| PLUMBING | [9 empty] | Instructions | User Comments | BPDA Comments
| Domestic/Service Hot Water | 5000 | MBH | (provide system description) | 50 | $/MBH (include all system costs) | 5000 | 250000 |  |  | Input the design domestic hot water capacity. Provide a description of the system and associated construction cost per unit listed.
| ELECTRICAL | [9 empty] | Instructions | User Comments | BPDA Comments
| Plant Peak Electrical Capacity | 1000 | kW | (provide system description) | 1500 | $/kW (include all system costs) | 1000 | 1500000 |  |  | Input the design electrical capacity to support the greater of ether the heating or cooling plant systems. Provide a description of the system and associated construction cost per unit listed.
| INCENTIVES | [9 empty] | Instructions | User Comments | BPDA Comments
| Total Year 1 Incentive Value |  |  | (provide incentive description) | -1.25 | $/sf | 0 | 0 |  |  | Input the total anticipated year-1 incentive value (utility, grants, other). Provide value in terms of $/sf.
2770000
|  | Performance / Quantity |  | System descriptions used for pricing | Construction Cost | Cost units | Quantity | Total Cost
Proposed Electric* | ARCHITECTURAL |  |  |  |  | Units |  |  |  |  | Instructions | User Comments | BPDA Comments
| Window (Glazing + Frame) |  |  | (same as Proposed) | 150 | $/sf window area | 0 | 0 |  |  | Automatic values, matching Proposed inputs above.
| Wall |  |  | (same as Proposed) | 115 | $/sf wall area | 0 | 0 |  |  | Automatic values, matching Proposed inputs above.
| Roof |  |  | (same as Proposed) | 30 | $/sf roof area | 0 | 0 |  |  | Automatic values, matching Proposed inputs above.
| Air Barrier Construction + Testing |  |  | (same as Proposed) | 0.5 | $/sf façade area | 0 | 0 |  |  | Automatic values, matching Proposed inputs above.
| Net Space Impact | -200 | area saved (SF) | (describe the space requirements compared to the proposed case) | 200 | $/sf floor area | 200 | 40000 |  |  | Approximate NET square footage savings (input positive value) [or increase (input negative value)] to accommodate smaller [or larger] mechanical and electrical systems within the building envelope. Do not include exterior areas, such as pad-mounted or roof-mounted equipment space requirements.
| HVAC | [9 empty] | Instructions | User Comments | BPDA Comments
| DOAS AHU | 0% | Heat Recovery | (provide system description) | 20 | $/cfm DOAS AHU capacity | 0 | 0 |  |  | The DOAS AHU system should match the Proposed design, except that the heat source should be changed to an all-electric source. This should be an integrated decision, accounting for the appropriate electric heating plant selection below.
| Non-DOAS AHU | 50000 | cfm | (provide system description) | 14 | $/cfm non-DOAS AHU capacity | 50000 | 700000 |  |  | The Non-DOAS AHU system should match the Proposed design, except that the heat source should be changed to an all-electric source. This should be an integrated decision, accounting for the appropriate electric heating plant selection below.
| Perimeter Heat | 8000 | lf | (provide system description) | 40 | $/lf perimeter heat (include riser + pump costs) | 8000 | 320000 |  |  | The perimeter heat system should match the Proposed design, except that the heat source should be changed to an all-electric source. This should be an integrated decision, accounting for the appropriate electric heating plant selection below.
| Zone Systems |  |  | (provide system description) | 5 | $/sf floor area | 0 | 0 |  |  | The zone heating and cooling system should match the Proposed design, except that the heat source should be changed to an all-electric source. This should be an integrated decision, accounting for the appropriate electric heating plant selection below.
| Electric Space Heating Plant | 1.7 | Air to Water | (provide system description) | 150 | $/MBH (include all plant costs) | #NUM! | #NUM! |  |  | Select the heat pump type from the drop-down menu, then provide a system description and cost (per unit of capacity listed).
| Non-Electric Space Heating Plant | n/a | n/a | n/a | n/a | n/a | n/a | n/a |  |  | This option assumes that the entire space-heating plant is electric. Therefore, this is not applicable.
| NON-Space-Heating Plant |  |  | (same as Proposed) | 30 | $/MBH (include all plant costs) | 0 | 0 |  |  | The NON-space-heating heating plant for the Proposed 100% Electric option shall match that of the Proposed design. This applies, even if the heating source is not electric.
| Cooling System | #NUM! | Tons | (provide system description) | 1000 | $/Ton (include all plant costs) | 1000 | 1000000 |  |  | The Proposed - 100% Electric option automatically calculates the cooling plant capacity, based on the Proposed design. It takes credit for the cooling capacity of the electric heat pump system. The cooling plant type should be determined based on engineering best practice, accounting for the Proposed cooling plant, the cooling plant capacity automatically calculated for the ZNC option, the electric heating plant type and associated cooling capacity, and optimal cost-effective integrated solutions.
| PLUMBING | [9 empty] | Instructions | User Comments | BPDA Comments
| Domestic/Service Hot Water |  |  | (provide system description) | 100 | $/MBH (include all system costs) Do not exceed 300% of Proposed option cost (see instructions) | 5000 | 500000 |  |  | The capacity of the ZNC option automatically matches the Proposed design. Users should input an appropriate electric domestic/service hot water system description and cost. If the domestic/service hot water system has high demand (such as would be the case for residential, hotel, healthcare, etc.), a hybrid electric/non-electric solution shall be utilized if necessary to avoid exceeding 300% of the domestic/service hot water system cost of the Proposed design. Include electrical infrastructure costs impacts in this assessment.
| ELECTRICAL | [9 empty] | Instructions | User Comments | BPDA Comments
| Plant Peak Electrical Capacity | #NUM! | kW | (provide system description) | 1500 | $/kW (include all system costs) | 1500 | 2250000 |  |  | The Proposed - 100% Electric option automatically calculates the value, based on the Proposed design, accounting for the net impact on electrical infrastructure due to the change in heating and cooling plant. It automatically takes into account whether the peak electrical demand is driven by cooling or heating.
| INCENTIVES | [9 empty] | Instructions | User Comments | BPDA Comments
| Total Year 1 Incentive Value |  |  | (provide incentive description) | -1.25 | $/sf | 0 | 0 |  |  | Input the total anticipated year-1 incentive value (utility, grants, other). Provide value in terms of $/sf.
*NON-Space-Heating Heating Plant and Domestic/Service Hot Water may be non-electric. | [7 empty] | #NUM!
MA Code n/a

## PRE-SUBMITTAL Dashboard
PRE-SUBMITTAL DASHBOARD
If the Proposed Heating Load is equal to or less than the Low Load Target AND the Proposed design is all electric, then you are done! If not, then complete the Development Review section.
For labs and healthcare only:
If the Proposed Heating Load is equal to or less than the Low Load Target AND the Proposed Electric Heat Pump Heating Capacity is equal to or greater than the 35°F Ambient Suggested Minimum Heat Pump Heating Capacity, then you are done! If not, then complete the Development Review section.
HEATING SYSTEM PROPOSED TO USE FOSSIL FUELS | LOAD EVALUATION |  |  | ASHRAE 90.1-2013
DHW SYSTEM PROPOSED TO USE FOSSIL FUELS |  | Low Load | Proposed
| Window-to-Wall Ratio (%) | #DIV/0! | #DIV/0! | 0%
| Window Assembly U-Value (Btu/h·F·sf) | 0.26 | 0 | 0.38
| Opaque Wall U-Value (Btu/h·F·sf) | 0.064 | 0 | 0.064
| Infiltration (cfm/sf at 75pa) | 0.1 | 0 | 0.25
| Roof Assembly R-Value (Btu/h·F·sf) | 0.032 | 0 | 0.032
| Ventilation Sensible Recovery (%) | #DIV/0! | #DIV/0! | #DIV/0!
| Building Heating Load (Btu/h·GSF) | #DIV/0! | #DIV/0! | #DIV/0!
| Primary System Oversize (%) | #NUM! | #NUM! | #NUM!
| HEATING CAPACITY TO BE ELECTRIFIED |  |  | ASHRAE 90.1-2013
|  | Low Load | Proposed
| Heating Load (Btu/h-GSF) to be Electrified | #DIV/0! | #DIV/0! | #DIV/0!
#DIV/0!
| LABS AND HEALTHCARE ONLY | Suggested Minimum (35°F Ambient)* | Proposed
| Electric Heat Pump Heating Capacity (Btu/h·GSF) | #NUM! | #DIV/0!
| Electric Heat Pump Heating Capacity (MBH) | #NUM! | 0 | #NUM!
| Electric Heat Pump % of Total Proposed Heating Load | #NUM! | #NUM!
| Overall Pass/Fail for Labs and Healthcare (must pass both criteria) |  |  | #DIV/0!
*The City of Somerville understands that it may not be practical to electrify 100% of the heating plant for high-ventilation facilities such as life sciences or healthcare buildings. Efficient systems and electrifying a portion of the heating plant equivalent to the load at 35°F will reduce fossil fuel consumption by upwards of 90%. The addition of heat pumps to satisfy this load will largely decarbonize high-ventilation load facilities in operation while allowing for combustion-based fuel sources to address peak heating conditions.

## DEVELOPMENT REVIEW INFO
DEVELOPMENT REVIEW INFO
New buildings and extensive renovations should ideally be designed to achieve operational
carbon neutrality and to minimize embodied carbon in construction materials.
This calculator provides an easy way to assess the operational emissions of your proposed design.
Instructions:
1 | Fill in the blue cells with the required information: |  |  |  |  | All user inputs in blue are required.
2 | Review the Development Review Dashboard tab.
3 | Compare the Proposed design to that of the MA Code Minimum design, and the 'Low Load' design.
4 | Consider strategies to cost-effectively reduce the loads of the Proposed design to bring it closer in line to the Low Load building.
| Energy Use Inputs | Site Annual Energy Consumption (MMBtu/yr) |  |  |  | Energy Use Intensity (kBtu/sf/yr)
| End Use Breakdown | Zero Carbon | Proposed | Proposed Electric* | ASHRAE 90.1-2013 | Low Load | Proposed | Proposed Electric* | ASHRAE 90.1-2013 | Fuel Type (drop-down menu) | Instructions | User Comments | Somerville Comments
| Lighting | not required |  |  |  | not required | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Plug Loads | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Fans | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Pumps | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Cooling | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Heating - Non-Electric 1 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Gas
| Heating - Non-Electric 2 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Gas
| Heating - Electric | [6 empty] | #DIV/0! |  | Electric
| DHW - Non-Electric 1 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Gas
| DHW - Non-Electric 2 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Gas
| DHW - Electric | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Process 1 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric | Process loads may include: pool heating, sterilization, humidification, etc.
| Process 2 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | Electric
| Process 3 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Process 4 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| On-site Renewables (negative) | [5 empty] | #DIV/0! | #DIV/0!
| Off-Site Renewables (negative) | [5 empty] | #DIV/0! | #DIV/0! |  | Renewable Electric Credit | Off-Site Renewable energy is limited to MA Class I RECs and minimum 15-year power purchase agreements for new renewable energy systems (installed within last 3 years) from grid regions with emissions factors at least as high as ISO-NE.
| TOTAL without Renewable Energy |  | 0 | 0 | 0 |  | #DIV/0! | #DIV/0! | #DIV/0!
| TOTAL with Renewable Energy |  | 0 | 0 | 0 |  | #DIV/0! | #DIV/0! | #DIV/0!
(if cogen is part of the proposed design, charge fuel consumption to Heating and credit electricity generation proportionally to all electric end uses)
| Emissions Outputs | Energy Consumption by Fuel (MMBtu/yr) |  |  |  | Current Carbon Emissions (metric tons CO2e/yr) |  |  |  | 2035 Carbon Emissions (metric tons CO2e/yr)
| Fuel Type | Low Load | Proposed | Proposed Electric* | ASHRAE 90.1-2013 | Zero Carbon | Proposed | Proposed Electric* | ASHRAE 90.1-2013 | Zero Carbon | Proposed | ASHRAE 90.1-2013
| Renewable Electric Credit | not required | 0 | 0 | 0 | not required | 0 | 0 | 0 | not required
| Electric |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
| Gas |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
| Oil |  | 0 | 0 | 0 |  | 0 | 0 | 0
| Propane |  | 0 | 0 | 0 |  | 0 | 0 | 0
| Other District Heating |  | 0 | 0 | 0 |  | 0 | 0 | 0
| District Cooling |  | 0 | 0 | 0 |  | 0 | 0 | 0
| Other Fuel 1 |  | 0 | 0 | 0 |  | 0 | 0 | 0
| Other Fuel 2 |  | 0 | 0 | 0 |  | 0 | 0 | 0
| TOTAL without Renewable Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL with Renewable Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Energy Use Intensity (kBtu/sf/yr) |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Emissions Intensity Outputs |  |  | Carbon Emissions Intensity (lbCO2e/yr·sf)
[6 empty] | Low Load | Proposed | Proposed Electric* | ASHRAE 90.1-2013
|  |  | TOTAL Without Renewable Energy |  |  | not required | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Renewable Energy Credit |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | TOTAL with Renewable Energy |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Carbon Emissions Factors for City of Somerville
| Fuel Type | lbCO2e/MMBtu | Value is based on:
| Renewable Electric Credit | 144.7335
| Electric | 144.7335 | Portfolio Manager Region Emissions Inensity. Note: this value will not match MEPA/DOER submissions, but it is used for LEED points.
| Electric 2035 | 114.8607
| Gas | 117 | US EIA value
| Oil | 161.3 | US EIA value
| Propane | 139.05 | US EIA value
| Other District Heating |  | User to calculate and input custom value.
| District Cooling |  | User to calculate and input custom value, based on the specific district chilled water system.
| Other Fuel 1 |  | User to calculate and input value for Other fuel type.
| Other Fuel 2 |  | User to calculate and input value for Other fuel type.
User to input description of Other Fuel type.
Footnotes:
1. Based on the latest ISO-NE Emissions Report. Should be updated as more recent ISO-NE Emissions Reports are available.
Graphic
|  | ASHRAE 90.1-2013 EUI | As-Designed EUI | % savings
| Lighting | #DIV/0! | #DIV/0! | 0%
| Plug Loads | #DIV/0! | #DIV/0! | 0%
| Fans | #DIV/0! | #DIV/0! | 0%
| Pumps | #DIV/0! | #DIV/0! | 0%
| Cooling | #DIV/0! | #DIV/0! | 0%
| Heating - Non-Electric 1 | #DIV/0! | #DIV/0! | 0%
| Heating - Electric |  |  | 0%
| DWH | #DIV/0! | #DIV/0! | 0%
| Process 1 | #DIV/0! | #DIV/0! | 0%
| On-site Renewables (negative) | 0 | #DIV/0!
| Off-Site Renewables (negative) | 0 | #DIV/0!
| TOTAL without Renewable Energy | #DIV/0! | #DIV/0!
| TOTAL with Renewable Energy | #DIV/0! | #DIV/0!

## DEVELOPMENT REVIEW Dashboard
DEVELOPMENT REVIEW DASHBOARD
| Proposed | ASHRAE 2013 | % Savings |  |  | LEED EAc1 Optimize Energy Performance Point Calculator**
Current Carbon Emissions Intensity (lbCO2e/yr-sf) | #DIV/0! | #DIV/0! | #DIV/0!
Site Energy Use (kBtu/sf/yr) | #DIV/0! | #DIV/0! | #DIV/0! |  | Please Select Rating system | LEED NC CS
Source Energy Use (kBtu/sf/yr) | #DIV/0! | #DIV/0! | #DIV/0! |  | Please Select Building Type | 900%
Annual Carbon Offsets to achieve ZNC (metric tons CO2e/yr) | 0 | 0 |  |  | Points earned | #DIV/0! | Min 10 pts***
2035 Carbon Emissions Intensity (lbCO2e/yr-sf)* | 0 | 0 | #DIV/0!
* A 40% savings CO2e emissions target (using 2035 emissions factors) has been established based on the findings of Built Environment Plus' "Massachusetts is Ready for Net Zero 2021 Report." The report surveyed over 7 Million GSF of Net-Zero buildings spanning a range of building types including K-12, Higher Education, Healthcare, Laboratory, Office, and Multifamily buildings in Massachusetts. The report findings indicate that a 40% savings in CO2e emissions, based on 2035 ISO-NE emissions rates, is a readily acheivable benchmark for high-performance buildings within the Greater Boston Area. The target represents the building-level operational carbon emissions reductions expected by the City of Somerville prior to the purchase of onsite or offsite renewable energy, or carbon offsets. **The City of Somerville requires projects to use the Alterntative Energy Performance Metric Pilot Credit EApc95 (https://www.usgbc.org/credits/eapc95v4). This compliance path allows projects to document performance improvements using Option 1 Whole Building Simulation and leverage an average of source energy and carbon emissions as an indicator of performance. The City prefers this compliance path as the considerations for CO2e emissions aligns with the City's Net Zero Performance goals. *** An EAc1 earning of at least 10 points is best poised to align with the City's CO2e and energy performance goas.

## Lookup Tables - LOCKED
Per ASHRAE 90.1-2019 Appendix G with MA Amendments (780 CMR revised 9th edition, mandatory as of January 2021)
Building Area Types Baseline Building Gross Above-Grade % Glazing | % | LEED NC CS | new construction | CS | BD+C | Healthcare | School | LEED NC BD+C | Add Points |  | Renewable Electric Credit
Grocery store | 7% | LEED NC BD+C | 6% | 3% | 1 | 3 | 1 | Office | 5% | Yes | Electric
Healthcare (outpatient) | 21% | LEED NC Healthcare | 8% | 5% | 2 | 4 | 2 | Retail (except restaurant/grocery) | 5% | No | Gas
Hospital | 27% | LEED NC Schools | 10% | 7% | 3 | 5 | 3 | School | 6% |  | Oil
Hotel/motel (≤75 rooms) | 24% |  | 12% | 9% | 4 | 6 | 4 | Healthcare | 3% |  | Propane
Hotel/motel (>75 rooms) | 34% |  | 14% | 11% | 5 | 7 | 5 | Restaurant/Grocery | 3% |  | Other District Heating
Office or Laboratory Building (≤5000 ft2) | 19% |  | 16% | 13% | 6 | 8 | 6 | Hospitality | 5% |  | District Cooling
Office or Laboratory Building (5000 to 50,000 ft2) | 31% |  | 18% | 15% | 7 | 9 | 7 | Warehouse | 1% |  | Other Fuel 1
Office or Laboratory Building (>50,000 ft2) | 40% |  | 20% | 17% | 8 | 10 | 8 | Multifamily | 3% |  | Other Fuel 2
Restaurant (quick service) | 34% |  | 22% | 19% | 9 | 11 | 9 | All Other | 2%
Restaurant (full service) | 24% |  | 24% | 21% | 10 | 12 | 10 | LEED NC CS | Add Points
Retail (stand alone) | 11% |  | 26% | 23% | 11 | 13 | 11 | Office | 3%
Retail (strip mall) | 20% |  | 29% | 26% | 12 | 14 | 12 | Retail (except restaurant/grocery) | 3%
School (primary) | 22% |  | 32% | 29% | 13 | 15 | 13 | School | 6%
School (secondary and university) | 22% |  | 35% | 32% | 14 | 16 | 14 | Healthcare | 1%
Warehouse (non-refrigerated) | 6% |  | 38% | 35% | 15 | 17 | 15 | Restaurant/Grocery | 2%
Multifamily | 24% |  | 42% | 39% | 16 | 18 | 16 | Hospitality | 3%
|  |  | 46% | 43% | 17 | 19 |  | Warehouse | 0%
|  |  | 50% | 47% | 18 | 20 |  | Multifamily | 1%
[8 empty] | All Other | 1%
Approximate value, based on technology available in 2020.
Heat Pump Electrical Infrastructure Design Demand Conversion Factor | COP
VRF | 2
Air to Water | 1.7
Exhaust-Source | 1.9

## Load Calculations - LOCKED
LOAD CALCULATIONS
This tab automatically creates the 'ZNC' and 'MA Code' options.
It then calculates the heating load associated with each option.
It also calculates the ventilation cooling load credit for the ZNC option.
Instructions:
1 | This tab must remain locked for submission to the City of Somerville
| Heating Load Outputs (Btu/h·GSF) | Low Load | Proposed | ASHRAE 90.1-2013
| Window Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| Wall Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| Roof Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| Infiltration | #NUM! | #NUM! | #NUM!
| Ventilation | #DIV/0! | #DIV/0! | #DIV/0!
| Oversize | #NUM! | #NUM! | #NUM!
| Total Space Heating System Load | #NUM! | #NUM! | #NUM!
| TOTAL Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| TOTAL Envelope | #NUM! | #NUM! | #NUM!
| NON-Space-Heating Plant Load | #DIV/0! | #DIV/0! | #DIV/0!
| Summary of Automatic Changes to Proposed Design | Low Load | Proposed | ASHRAE 90.1-2013
| Total Building - Window to Wall Ratio | #DIV/0! | #DIV/0! | 0%
| Window Average Assembly U-value (Btu/h·∆T·sf) | 0.26 | 0 | 0.38
| Wall Average Assembly U-value (Btu/h·∆T·sf) | 0.064 | 0 | 0.064
| Roof Average Assembly U-value (Btu/h·∆T·sf) | 0.032 | 0 | 0.032
| Infiltration - Maximum at Blower Door Test (cfm/sf at 75pa) | 0.1 | 0 | 0.25
| Proposed Outdoor Airflow Rate (CFM) | 0 | 0 | 0
| Ventilation Heating Sensible Recovery Efficiency | 80% | 0% | 50%
| Class 3 and 4 Exhaust Sensible Recovery Efficiency | 55% | 0% | 0%
| Electric Heating System Capacity (Btu/h·gsf) | 0 | #DIV/0! | 0
| Oversize Factor: Heating System Capacity / Heating Load (%) | 125% | #NUM! | 125%
| General Information | Low Load | Proposed | ASHRAE 90.1-2013
| Number of Stories Above Grade | 0 | 0 | 0
| Total Building Gross Floor Area | 0 | 0 | 0
| Total Building Net Occupiable Floor Area | 0 | 0 | 0
| Daylight Area (per IECC 2018) | 0 | 0 | 0
| Total Building Vertical Façade Area | 0 | 0 | 0
| Roof Area | 0 | 0 | 0
| Primary Building Type | Low Load | Proposed | ASHRAE 90.1-2013
| Primary Building Type | 0 | 0 | 0
| Gross Square Feet | 0 | 0 | 0
| Vertical Façade Area | 0 | 0 | 0
| Window Area | n/a | 0 | n/a
| Secondary Building Type | Low Load | Proposed | ASHRAE 90.1-2013
| Secondary Building Type | 0 | 0 | 0
| Gross Square Feet | 0 | 0 | 0
| Vertical Façade Area | 0 | 0 | 0
| Window Area | n/a | 0 | n/a
| Tertiary Building Type | Low Load | Proposed | ASHRAE 90.1-2013
| Tertiary Building Type | 0 | 0 | 0
| Gross Square Feet | 0 | 0 | 0
| Vertical Façade Area | 0 | 0 | 0
| Window Area | n/a | 0 | n/a
| Daylight Area | Low Load | Proposed | ASHRAE 90.1-2013
| % Daylight Area | 0% | 0% | 0%
| Daylight Area >25%? (or >50% if building is <3 stories above grade) | No | No | No
| Envelope | Low Load | Proposed | ASHRAE 90.1-2013
| Total Vertical Façade Area | 0 | 0 | 0
| Primary Building - Window to Wall Ratio | 0% | 0% | n/a
| Secondary Building - Window to Wall Ratio | 0% | 0% | n/a
| Tertiary Building - Window to Wall Ratio | 0% | 0% | n/a
| Total Building - Window to Wall Ratio | #DIV/0! | #DIV/0! | 0%
| Total Window Area | 0 | 0 | 0
| Window Average Assembly U-value (Btu/h·∆T·sf) | 0.26 | 0 | 0.38
| Wall Area (SF) | 0 | 0 | 0
| Wall Average Assembly U-value (Btu/h·∆T·sf) | 0.064 | 0 | 0.064
| Roof Area (SF) | 0 | 0 | 0 | Infiltration
| Roof Average Assembly U-value (Btu/h·∆T·sf) | 0.032 | 0 | 0.032 | P stack average on building | 0 | Pa
| Infiltration - Maximum at Blower Door Test (cfm/sf at 75pa) | 0.1 | 0 | 0.25 | P stack | 0 | Pa
| Infiltration - Maximum at Blower Door Test (cfm at 75pa) | 0 | 0 | 0 | P wind | 2.2336 | Pa
| Infiltration - Design (cfm) | #NUM! | #NUM! | #NUM! | P mech | -5 | Pa
| Average UxA Value2 | #DIV/0! | #DIV/0! | #DIV/0! | Reference Wind Speed | 4.47 | m/s
[5 empty] | γ | 0.65
| Ventilation | Low Load | Proposed | ASHRAE 90.1-2013 | Outdoor temperature | -17.7 | °C
| Minimum Outdoor Airflow Rate (CFM) | 0 | 0 | 0 | Outdoor air density | 1.3826 | kg/m3
| Minimum Outdoor Airflow Rate (CFM/Net SF) | #DIV/0! | #DIV/0! | #DIV/0! | Indoor temperature | 20 | °C
| Proposed Outdoor Airflow Rate (CFM) | 0 | 0 | 0 | Indoor air density | 1.2047 | kg/m3
| Proposed Outdoor Airflow Rate (CFM/Net SF) | n/a | #DIV/0! | n/a | g | 9.81
| Exhaust/Relief Air (not including Class 3 and 4 and Exempt Exhaust) | 0 | 0 | 0 | Building height | 0 | ft
| Ventilation Heating Sensible Recovery Efficiency | 80% | 0% | 50%
| Class 3 and 4 Exhaust (CFM) | 0 | 0 | 0
| Class 3 and 4 Exhaust Sensible Recovery Efficiency | 55% | 0% | 0%
| Exempt Exhaust (CFM) | 0 | 0 | 0
| Exempt Exhaust Heat Recovery Efficiency | 0% | 0% | 0%
| Average Exhaust Heat Recovery Efficiency | #DIV/0! | #DIV/0! | #DIV/0!
| Heating Load | Low Load | Proposed | ASHRAE 90.1-2013
| Delta-T (°F Outdoor - °F Indoor) | 70 | 70 | 70
| Window Conduction Heating Load (MBH) | 0 | 0 | 0
| Wall Conduction Heating Load (MBH) | 0 | 0 | 0
| Roof Conduction Heating Load (MBH) | 0 | 0 | 0
| Envelope Infiltration Heating Load (MBH) | #NUM! | #NUM! | #NUM!
| Ventilation Heating Load (MBH) | #DIV/0! | #DIV/0! | #DIV/0!
| Safety Factor (MBH) | #NUM! | #NUM! | #NUM!
| TOTAL Space Heating System Load (MBH) | #NUM! | #NUM! | #NUM!
| Total Envelope Conduction Heating Load (MBH) | 0 | 0 | 0
| Maximum Electric Heating System Capacity (Btu/h·gsf) | n/a | n/a | n/a
| Electric Heating System Capacity (Btu/h·gsf) | 0 | #DIV/0! | 0
| Electric Heating System Capacity (MBH) | 0 | 0 | n/a
| Other Heating System Capacity (MBH) | #NUM! | 0 | #NUM!
| TOTAL Heating System Capacity (MBH) | n/a | 0 | n/a
| Oversize Factor: Heating System Capacity / Heating Load (%) | 125% | #NUM! | 125%
| NON-Space-Heating Plant Capacity (MBH) | 0 | 0 | 0
| Ventilation Cooling Load | Low Load | Proposed | ASHRAE 90.1-2013
| Outdoor Air - Temperature (°F) | 91 | 91 | 91
| Outdoor Air - Wet Bulb (°F) | 73 | 73 | 73
| Outdoor Air - Enthalpy (Btu/lb) | 36.48 | 36.48 | 36.48
| Indoor Air - Temperature (°F) | 75 | 75 | 75
| Indoor Air - Relative Humidity (%) | 55% | 55% | 55%
| Indoor Air - Enthalpy (Btu/lb) | 29.13 | 29.13 | 29.13
| Ventilation Cooling Enthalpy Recovery Efficiency (%) | 77.5% | 0% | 50%
| Ventilation Air after Energy Recovery - Enthalpy (Btu/lb) | 30.7837 | 36.48 | 32.805
| Ventilation Discharge Air Enthalpy (Btu/lb) | 22.13 | 22.13 | 22.13
| Ventilation Delta H (Btu/cfm) | 8.6537 | 14.35 | 10.675
| Ventilation Cooling Load (Btu/cfm) | 38.9419 | 64.575 | 48.0375
| Ventilation Cooling Load (Tons) | 0 | 0 | 0
| Class 3 and 4 Exhaust Sensible Heat Recovery Efficiency (%) | 55% | 0% | 0%
| Class 3 and 4 Exhaust Make Up - Temperature after Energy Recovery (°F) | 82.2 | 91 | 91
| Class 3 and 4 Exhaust Make-Up Load Reduction (Tons) | 0 | 0 | 0
| Total Load Reduction (Tons) | 0 | 0 | 0
| DHW Loads | Low Load | Proposed | ASHRAE 90.1-2013
| DHW - Non-Electric 1 - (MMBtu/yr) |  | 0 | 0
| DHW - Non-Electric 2 (MMBtu/yr) |  | 0 | 0
| DHW - Electric (MMBtu/yr) |  | 0 | 0
| TOTAL DHW Heating System Capacity (MMBtu/yr) |  | 0 | 0
| PERCENT DHW - Gas |  | #DIV/0! | #DIV/0!
| PERCENT DHW - Electric |  | #DIV/0! | #DIV/0!

## 35F Ambient Loads - LOCKED
LOAD CALCULATIONS
This tab automatically creates the 'ZNC' and 'MA Code' options.
It then calculates the heating load associated with each option.
It also calculates the ventilation cooling load credit for the ZNC option.
Instructions:
1 | This tab must remain locked for submission to the City of Somerville
| Heating Load Outputs (Btu/h·GSF) | Low Load ZNC | Proposed | MA Code
| Window Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| Wall Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| Roof Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| Infiltration | #NUM! | #NUM! | #NUM!
| Ventilation | #DIV/0! | #DIV/0! | #DIV/0!
| Oversize | #NUM! | #NUM! | #NUM!
| Total Space Heating System Load | #NUM! | #NUM! | #NUM!
| TOTAL Conduction | #DIV/0! | #DIV/0! | #DIV/0!
| TOTAL Envelope | #NUM! | #NUM! | #NUM!
| NON-Space-Heating Plant Load | #DIV/0! | #DIV/0! | #DIV/0!
| Summary of Automatic Changes to Proposed Design | Low Load ZNC | Proposed | MA Code
| Total Building - Window to Wall Ratio | #DIV/0! | #DIV/0! | 0%
| Window Average Assembly U-value (Btu/h·∆T·sf) | 0.26 | 0 | 0.38
| Wall Average Assembly U-value (Btu/h·∆T·sf) | 0.064 | 0 | 0.064
| Roof Average Assembly U-value (Btu/h·∆T·sf) | 0.032 | 0 | 0.032
| Infiltration - Maximum at Blower Door Test (cfm/sf at 75pa) | 0.1 | 0 | 0.25
| Proposed Outdoor Airflow Rate (CFM) | 0 | 0 | 0
| Ventilation Heating Sensible Recovery Efficiency | 80% | 0% | 50%
| Class 3 and 4 Exhaust Sensible Recovery Efficiency | 60% | 0% | 0%
| Electric Heating System Capacity (Btu/h·gsf) | #NUM! | 0 | 0
| Oversize Factor: Heating System Capacity / Heating Load (%) | 125% | 125% | 125%
| General Information | Low Load ZNC | Proposed | MA Code
| Number of Stories Above Grade | 0 | 0 | 0
| Total Building Gross Floor Area | 0 | 0 | 0
| Total Building Net Occupiable Floor Area | 0 | 0 | 0
| Daylight Area (per IECC 2018) | 0 | 0 | 0
| Total Building Vertical Façade Area | 0 | 0 | 0
| Roof Area | 0 | 0 | 0
| Primary Building Type | Low Load ZNC | Proposed | MA Code
| Primary Building Type | 0 | 0 | 0
| Gross Square Feet | 0 | 0 | 0
| Vertical Façade Area | 0 | 0 | 0
| Window Area | n/a | 0 | n/a
| Secondary Building Type | Low Load ZNC | Proposed | MA Code
| Secondary Building Type | 0 | 0 | 0
| Gross Square Feet | 0 | 0 | 0
| Vertical Façade Area | 0 | 0 | 0
| Window Area | n/a | 0 | n/a
| Tertiary Building Type | Low Load ZNC | Proposed | MA Code
| Tertiary Building Type | 0 | 0 | 0
| Gross Square Feet | 0 | 0 | 0
| Vertical Façade Area | 0 | 0 | 0
| Window Area | n/a | 0 | n/a
| Daylight Area | Low Load ZNC | Proposed | MA Code
| % Daylight Area | 0% | 0% | 0%
| Daylight Area >25%? (or >50% if building is <3 stories above grade) | No | No | No
| Envelope | Low Load ZNC | Proposed | MA Code
| Total Vertical Façade Area | 0 | 0 | 0
| Primary Building - Window to Wall Ratio | 0% | 0% | n/a
| Secondary Building - Window to Wall Ratio | 0% | 0% | n/a
| Tertiary Building - Window to Wall Ratio | 0% | 0% | n/a
| Total Building - Window to Wall Ratio | #DIV/0! | #DIV/0! | 0%
| Total Window Area | 0 | 0 | 0
| Window Average Assembly U-value (Btu/h·∆T·sf) | 0.26 | 0 | 0.38
| Wall Area (SF) | 0 | 0 | 0
| Wall Average Assembly U-value (Btu/h·∆T·sf) | 0.064 | 0 | 0.064
| Roof Area (SF) | 0 | 0 | 0 | Infiltration
| Roof Average Assembly U-value (Btu/h·∆T·sf) | 0.032 | 0 | 0.032 | P stack average on building | 0 | Pa
| Infiltration - Maximum at Blower Door Test (cfm/sf at 75pa) | 0.1 | 0 | 0.25 | P stack | 0 | Pa
| Infiltration - Maximum at Blower Door Test (cfm at 75pa) | 0 | 0 | 0 | P wind | 2.0761 | Pa
| Infiltration - Design (cfm) | #NUM! | #NUM! | #NUM! | P mech | -5 | Pa
| Average UxA Value2 | #DIV/0! | #DIV/0! | #DIV/0! | Reference Wind Speed | 4.47 | m/s
[5 empty] | γ | 0.65
| Ventilation | Low Load ZNC | Proposed | MA Code | Outdoor temperature | 1.67 | °C
| Minimum Outdoor Airflow Rate (CFM) | 0 | 0 | 0 | Outdoor air density | 1.2851 | kg/m3
| Minimum Outdoor Airflow Rate (CFM/Net SF) | #DIV/0! | #DIV/0! | #DIV/0! | Indoor temperature | 20 | °C
| Proposed Outdoor Airflow Rate (CFM) | 0 | 0 | 0 | Indoor air density | 1.2047 | kg/m3
| Proposed Outdoor Airflow Rate (CFM/Net SF) | n/a | #DIV/0! | n/a | g | 9.81
| Exhaust/Relief Air (not including Class 3 and 4 and Exempt Exhaust) | 0 | 0 | 0 | Building height | 0 | ft
| Ventilation Heating Sensible Recovery Efficiency | 80% | 0% | 50%
| Class 3 and 4 Exhaust (CFM) | 0 | 0 | 0
| Class 3 and 4 Exhaust Sensible Recovery Efficiency | 60% | 0% | 0%
| Exempt Exhaust (CFM) | 0 | 0 | 0
| Exempt Exhaust Heat Recovery Efficiency | 0% | 0% | 0%
| Average Exhaust Heat Recovery Efficiency | #DIV/0! | #DIV/0! | #DIV/0!
| Heating Load | Low Load ZNC | Proposed | MA Code
| Delta-T (°F Outdoor - °F Indoor) | 35 | 35 | 35
| Window Conduction Heating Load (MBH) | 0 | 0 | 0
| Wall Conduction Heating Load (MBH) | 0 | 0 | 0
| Roof Conduction Heating Load (MBH) | 0 | 0 | 0
| Envelope Infiltration Heating Load (MBH) | #NUM! | #NUM! | #NUM!
| Ventilation Heating Load (MBH) | #DIV/0! | #DIV/0! | #DIV/0!
| Safety Factor (MBH) | #NUM! | #NUM! | #NUM!
| TOTAL Space Heating System Load (MBH) | #NUM! | #NUM! | #NUM!
| Total Envelope Conduction Heating Load (MBH) | 0 | 0 | 0
| Maximum Electric Heating System Capacity (Btu/h·gsf) | 10 | n/a | n/a
| Electric Heating System Capacity (Btu/h·gsf) | #NUM! | 0 | 0
| Electric Heating System Capacity (MBH) | #NUM! | 0 | n/a
| Other Heating System Capacity (MBH) | #NUM! | 0 | #NUM!
| TOTAL Heating System Capacity (MBH) | n/a | 0 | n/a
| Oversize Factor: Heating System Capacity / Heating Load (%) | 125% | 125% | 125%
| NON-Space-Heating Plant Capacity (MBH) | 0 | 0 | 0
| Ventilation Cooling Load | Low Load ZNC | Proposed | MA Code
| Outdoor Air - Temperature (°F) | 91 | 91 | 91
| Outdoor Air - Wet Bulb (°F) | 73 | 73 | 73
| Outdoor Air - Enthalpy (Btu/lb) | 36.48 | 36.48 | 36.48
| Indoor Air - Temperature (°F) | 75 | 75 | 75
| Indoor Air - Relative Humidity (%) | 55% | 55% | 55%
| Indoor Air - Enthalpy (Btu/lb) | 29.13 | 29.13 | 29.13
| Ventilation Cooling Enthalpy Recovery Efficiency (%) | 77.5% | 0% | 50%
| Ventilation Air after Energy Recovery - Enthalpy (Btu/lb) | 30.7837 | 36.48 | 32.805
| Ventilation Discharge Air Enthalpy (Btu/lb) | 22.13 | 22.13 | 22.13
| Ventilation Delta H (Btu/cfm) | 8.6537 | 14.35 | 10.675
| Ventilation Cooling Load (Btu/cfm) | 38.9419 | 64.575 | 48.0375
| Ventilation Cooling Load (Tons) | 0 | 0 | 0
| Class 3 and 4 Exhaust Sensible Heat Recovery Efficiency (%) | 60% | 0% | 0%
| Class 3 and 4 Exhaust Make Up - Temperature after Energy Recovery (°F) | 81.4 | 91 | 91
| Class 3 and 4 Exhaust Make-Up Load Reduction (Tons) | 0 | 0 | 0
| Total Load Reduction (Tons) | 0 | 0 | 0

## Emissions Sources - LOCKED
Electricity CO2e Emissions Comparison
Source | Listed Units | Listing | lb/MMBtu
Portfolio Manager (August 2021) | kg/Mbtu* | 70.13 | 144.7335
ISO-NE 2019 | lbs/MWh | 633 | 185.5217
ISO-NE 2035 (projected per city of Boston proposed Zero Carbon Zoning) | kg/MMBtu | 52.1 | 114.8607